IRC4 hands-on

2oo3
MPS Configuration :
MPC4 on slot3 :

Transducer1 on Input n° 1 – (ADC) Relativ Vibration

· Danger+ set to 500um, enabled and not latched

· Transducer1 SOK ( OC Bus 1

· Transducer1 Danger+ ( OC Bus 2  

MPC4 on slot4 :

Transducer2 on Input n° 1 – (ADC) Relativ Vibration

· Danger+ set to 500um, enabled and not latched

· Transducer2 SOK ( OC Bus 3

· Transducer2 Danger+ ( OC Bus 4

MPC4 on slot6 :

Transducer3 on Input n° 1 – (ADC) Relativ Vibration

· Danger+ set to 500um, enabled and not latched

· Transducer3 SOK ( RAW Bus 1

· Transducer3 Danger+ ( RAW Bus 2

RLC16 on slot 1 (Rack rear layout)


OC Bus ( Bus A

· Slot 3 : (MCR) to Relay 1 (NE)

· Slot 3 : (V1SOK) to Relay 2 (NE)

· Slot 3 : (V11D+) to Relay 3 (NE)

· Slot 4 : (MCR) to Relay 4 (NE)

· Slot 4 : (V1SOK) to Relay 5 (NE)

· Slot 4 : (V11D+) to Relay 6 (NE)

Discret Information ( Raw Bus

· Slot 6 : (MCR) to Line 32/Relay 1 RLC Slot 1 (NE)

· Slot 6 : (V1SOK) to Line0/Relay 2 RLC Slot 1 (NE)

· Slot 6 : (V11D+) to Line33/Relay 3 RLC Slot 1 (NE)

Logic :

RL1_LOGIC is true if :
Two transducers over trip level when all three transducers OK.

OR One transducers over trip level when two transducers OK (one NotOK).

OR Two transducers NotOK.

RL1_RESET:

Not used

Step-by-step guide:
- IRC4 Configurator installation :

- The installation files are located there :


ftp://vmchftp.vibro-meter.com 



user:     gcla



password: n!ght.09


- Refer to the installation procedure of the Software Manual (chapter 2).

- Create a test rack on the MPS with the 3 MPC4 cards described above .

- Mapping extraction of the RAW/OC busses

- using the tools "MPS - backplane configuration extractor" check the mapping

 
- open a DOS windows (Start ( Programs ( Accesories ( Command prompt)

- If needed refer to one of the various tutorial about « using DOS command line » 

e.g. http://csjava.occ.cccd.edu/~gilberts/jdkinstall/DOS.html

- Refer to the « MPS - backplane configuration extractor » chapter of the Software Manual
- Completion of the excel file


- Use the appendix « Reserved word » and the chapter « Creating the .xls and .rck files » of the Software Manual.

- Import the .xls and the .rck using the IRC4 Configurator.

- File compilation and simulation of the logic.

- Download to board and test with the board
