| Date | Card PNR | Firmware version / PNR | Change | Description |
| --- | --- | --- | --- | --- |
| November 2017 | 200-595-080-xxx | 80 / 209-595-400-080 (PFM-541I) and 209-595-300-080 (MSM586) | Bug fix | System: 1. Changed the PROFIBUS polling rates for the Modbus server to 100 ms (instead of 200 ms, to be consistent with our 'standard' Modbus server polling rate). 2. Fixed a known time counter wraparound (overflow) issue. (More specifically, the counter wraps around (jumps back to zero) after a CPUx card has been running continuously, as follows: after every 49 days 17 hours 2 minutes and 47 seconds for a CPUM card and after every 24 days 20 hours 31 minutes and 23 seconds for a CPUR card.) Note: The wraparound issue was first noticed in combustion monitoring aplications that use a CPUx card’s heartbeat register to generate a time counter that was communicated by PROFIBUS to an external control system that is part of a combustion monitoring system. Refer to the ‘VM600 CPUx time counter wraparound (overflow)’ service bulletin (CPUx-001) for further information. 3. Security improvements as follows: (i) Remove unused user accounts ('pppuser', 'ftpuser' and 'opig') with weak passwords. (ii) Prevent logins using the 'bin' user account which has no password at all. See PCR 17173 for further information. |
|  |  |  | Compatibility | This firmware release (080) is compatible with all possible hardware configurations of the CPUM card using the PFM-541I or MSM586 CPU module. (This version does not support the older MSM486 CPU module.) For information on CPUM card firmware and VM600 MPS software compatibility, refer to the latest version of the VM600 MPS software release notes. Note: This version is based on the 079 version of firmware. |